`

| Meeting Date | 29th August 2023 |  | Agenda Item |  |  | 5.1 |
| --- | --- | --- | --- | --- | --- | --- |
| Report Title | Estates Assurance Report |  |  |  |  |  |
| Report Author | Des Keighan, Assistant Director of Estates |  |  |  |  |  |
| Report Sponsor | Darren Griffiths, Director of Finance & Performance |  |  |  |  |  |
| Presented by | Darren Griffiths, Director of Finance & Performance |  |  |  |  |  |
| Freedom of Information | Open |  |  |  |  |  |
| Purpose of the Report | The purpose of this report is to provide an update on the range of activities undertaken in respect of the management of the Health Board’s estate. |  |  |  |  |  |
| Key Issues | Previous iterations of this report were routinely received at the Health and Safety Committee. The report provides an update on key operational matters relating to the management of the Health Board’s estate. The key areas covered in this report are: - - Backlog maintenance - Asbestos management - Water safety - Medical gas pipeline systems - Electrical services - Ventilation systems - Decontamination - Security - Fire safety - Waste management - Maintenance services - Energy - Audit The report contains a considerable amount of detail as it is the first time that the Performance and Finance Committee will have received such a report. It would be helpful to take a steer on the level of detail and nature of reporting the committee would wish to see in future for assurance purposes. |  |  |  |  |  |
| Specific Action Required (please choose one only) | Information | Discussion |  | Assurance | Approval |  |
|  | ☐ | ☐ |  | ☒ | ☐ |  |
| Recommendations | Members are asked to: - NOTE the report |  |  |  |  |  |

ESTATES ASSURANCE REPORT

- INTRODUCTION

The purpose of this report is to provide an update on the range of activities undertaken in respect of the management of the Health Board’s estate.

Previous iterations of this report were routinely received at the Health and Safety Committee.

The report contains a considerable amount of detail as it is the first time that the Performance and Finance Committee will have received such a report. It would be helpful to take a steer on the level of detail and nature of reporting the committee would wish to see in future for assurance purposes.

- BACKGROUND

This section of the report provides an update across all the key areas of work undertaken by the estates team.

- Backlog maintenance

The Health Board has undertaken a six-facet survey of its entire estate to provide a benchmark for its services.  The survey looks at the estate across six key parameters, those being its condition, statutory compliance, space utilisation, function suitability, energy and quality.  From this review we are able to identify our backlog maintenance under the risk-based approach to back log maintenance, in which there are key criteria against which the estate is judged.  From an estates point of view, the objective is to have the physical estate in Condition B.  Condition B requires little or minor upgrading.  From this review the Health Board has identified a cost non-risk adjusted of £125million to bring the estate up to Condition B, over a range of services which are summarised in the table below.

| Category | Sum of Cost |
| --- | --- |
| A - Building - Physical Structure | £ 110,000.00 |
| B1 - Building - External Fabric | £ 1,181,750.00 |
| B2 - Building - External Fabric | £ 5,314,450.00 |
| C - Building - Internal Fabric | £ 25,736,680.00 |
| D - Building - Roof – Flat | £ 2,957,000.00 |
| D - Building - Roof – Pitched | £ 4,177,480.00 |
| F - Building - External Works | £ 2,316,705.00 |
| H - Engineering – Drainage | £ 130,000.00 |
| I - Engineering - Heating Systems | £ 8,620,650.00 |
| J - Engineering - Steam Systems | £ 70,000.00 |
| K - Engineering - Vent & Cooling | £ 11,946,000.00 |
| L - Engineering - Medical Gases | £ 2,157,000.00 |
| M - Engineering - Hot/Cold Water | £ 4,626,550.00 |
| N - Engineering – Lifts | £ 3,765,000.00 |
| O - Engineering - Medical Systems | £ 4,100,000.00 |
| R - Engineering – Electrical | £ 12,894,250.00 |
| V - Engineering - Fire Systems | £ 5,312,450.00 |
| W - Engineering - Telecoms & Security | £ 47,000.00 |
| X - Engineering - Fuel Storage | £ 115,000.00 |
| X - Fuel Storage | £ 2,000.00 |
| Z - Statutory Compliance | £ 30,066,910.00 |
| Grand Total | £ 125,646,875.00 |

These costs are the raw cost to carry out the work and do not include overheads, fees or any enabling works.  Therefore, costs can vary by up to 120%.  The Health Board has developed an estates strategy that sets out how the Health Board will address the issues identified through the development of its estate.

The estates function has a duty to ensure that engineering services are maintained in accordance with both Legislation and with the Hospital Technical Memorandum (HTM), which are effectively the industry guidelines.  The Health Board has identified a number of key elements that have to be managed as specialist functions. These are: -

- Asbestos

- Water

- Medical gases

- High voltage and low voltage electricity

- Ventilation

- Decontamination

- Security

- Fire

For each of these specialities the Health Board has subgroups which have been established to ensure that the Health Board discharges its duties in these areas.

A number of these services require the appointment of a designated person for all estates issues, which is the Director of Finance and Performance, and a Senior Operational Manager (SOM) who takes professional responsibility of the estate, with this role being undertaken by the Assistant Director of Estates.  The Assistant Director of Estates is supported by Authorised Persons (AP’s) who have attended appropriate training, have been independently assessed and appointed in writing, to undertake these duties for specific functions of the estate.  Currently one of the key issues, due to lack of staff, is an inability to recruit to a number of positions, and as a result of guidance on how many of these AP duties an individual can take, we have insufficient AP’s for specific disciplines on the Morriston site.

Detailed below is the current status on each of these specialities:

- Asbestos Management

The Health Board is undertaking reviews of the asbestos management plans, which are updated on an annual basis.  Within this financial year, we have allocated £100,000 through Estates Funding Advisory Board (EFAB) funding to address these issues.  The investment this year will focus on the roof void within Philips Parade and an area of underground duct beneath Ward 1 in Singleton Hospital. Next financial year, the Health Board has been successful in securing £200,000 worth of investment and will be working through plans on where this will be prioritised over the coming months.

For asbestos management there is a sub-group of the Health and Safety Operational Group that meets on a quarterly basis, with representatives from the two estates departments, Health and Safety and the estates Health and Safety Officer.

Terms of reference are available for all of the groups should the committee wish to see these.

Key Issues and Mitigation

- Clearly Singleton Hospital presents the most challenges due to the number of areas that are affected by the presence of asbestos.  Whilst we have clear protocols to mitigate any risk, the presence of asbestos in the voids present significant operational difficulties.  Simple blockages cannot be addressed by the estates staff but require the attendance of specialist contractors licenced to work within these areas.  All voids within the Singleton site have restricted access due to the presence of asbestos.

- Water

The Health Board completed water risk assessments for the entire estate in 2022 which identified a number of risks and recommended actions to be taken.  The Health Board has secured EFAB funding to address these issues.  This year the priorities have been identified as Outpatients in Singleton Hospital and Cimla Hospital, in which work will be taking place to address the issues identified in these areas.

The Health Board Water Management group is chaired by the Director of Performance and Finance and meets on a quarterly basis.  It is made up of representatives from the two estates departments, Authorising Engineer (AE) Water, service units, Infection Prevention, Capital, as well as Authorised Persons (AP’s) from each site.

Key Issues and Mitigation

- Welsh Water have visited both the Morriston and Singleton site and have issued a list of remedial works they require undertaking.  Both sites are working through these documents.  As part of the departments mitigation of this issue, the bid for capital funding has been made to support expediting the works.

- The Health Board has implemented a programme of Legionella testing and are looking to increase the level of Pseudomonas testing in augmented care areas.  Specifically in Ward 12 due to an increased incident of contamination in that area.  Pseudomonas tend to originate from contamination of the outlet rather than from the water.  The additional cost has been highlighted to the Director of Finance and Performance, however as this was a recommendation from the Water Safety Committee the additional cost has been agreed.

- Although Singleton have AP’s in place, as does Morriston, there is an issue with the number of AP’s within the Morriston site.  The department have been trying to recruit additional Estates Officers; however, this has been proving difficult in the current market.  The department have recruited more Estates Officers; however we are still out for advert for the fourth time to recruit to existing vacancies which will help address this issue.

- Medical Gas Pipeline Systems

The Medical Gas Group is chaired by the Deputy Chief Operating Officer on behalf of the Director of Performance and Finance and meets on a quarterly basis.  It is made up of representatives from the two estates departments, service units, Pharmacy, Support Services, Quality Control Pharmacist, midwifery, theatres, as well as the AP’s from each site.

We have AP’s appointed on both sites; however, we still are short on AP’s on the Morriston site.  This has been exacerbated as a result of the vacancies within the department.

Key Issues and Mitigation

- The updating of the policy and the development of site specific standing operating procedures.  The revised policy has been re-drafted and it is hoped that this will be approved at the next Medical Gas Committee held in September, prior to submission to this committee for ratification.

- The removal of nitrous oxide piped medical gas systems - this is being investigated as a result of the carbon impact from these gases.

- Training for the medical staff on their roles and responsibilities for the medical gas system.  The Assistant Director of Estates working with the Head of EBME have put together a training programme for the staff and are working with the service groups to get agenda time within the existing meeting frameworks.  The Head of EBME has developed a new medical gas training package that is being put onto ESR at a national level, with a view to rolling this out as a standard requirement for nursing staff.

- Electrical Services – High (HV) and Low Voltage (LV)

There are issues on both sites with regards to electrical services and their compliance with the Welsh Health Technical Memorandums (WHTM’s).  A number of the systems, by nature of their design and age, do not comply with latest guidance.  There are loading issues on the Morriston site, however it is hoped that the work being completed on Sub Station 6 (a development approved by the Health Board and funded by Welsh Government (WG)) will help to address this issue.

As part of the 6-Facet review £12.8million of cost was identified to upgrade and renew the existing electrical systems across the Health Board.  These works were part of the submission to Welsh Government as part of the estates strategy approved by the Board.

The Electrical Group is chaired by the Assistant Director of Estates and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE’s for HV and LV and Capital.

Key Issues and Mitigation

- Lack of sufficient AP’s on the Morriston site.  The department has recruited more Estates Officers; however, we are still out for advert for the fourth time to recruit to existing vacancies which will help address this issue.

- Remedial works on Sub 2.  This has been allocated capital to address some of the issues.

- Sub 6 development.  This is currently being overseen by Capital colleagues.

- Ventilation Systems

The last Audit Report highlighted the fact that a large proportion of our plant is non-compliant with the current WHTM’s, noting that the plant was not designed to meet the current standards.  These shortcomings have been highlighted in the Estates strategy which has now been approved by the Board.  The Chief Executive Officer and Director of Finance and Performance have now presented the Estates Strategy to the Welsh Government for their consideration.  This outlines the capital required to deliver the changes required.

The Ventilation Group is chaired by the Assistant Director of Estates and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE Vent, Capital and Health and safety.

Key Issues and Mitigation

- Throughout the Morriston site, the ward areas ventilation systems were not designed to deliver the air change rates recommended since the pandemic.  Their design is predicated on providing air changes to the core areas which is supplemented by opening windows.  This has been recognised within the backlog maintenance costs developed under the 6-Facet survey.  This forms part of the plans detailed within the Estates Strategy which has been shared with the Welsh Government, seeking funding of over £840 million to address backlog maintenance issues.

- Some of the recent guidance suggests the use of air scrubbers where ventilation rates don’t meet the recent recommendations,  However concern has been expressed over the practically of this approach due to three main reasons.  1. The electrical load that this would generate and the ability to support this2  2.  The noise from the units and the disruption that may give to patients.  3. Infection control protocols around the units of this type.  Trials of units in some of the dental units are being undertaken,

- Lack of sufficient AP’s on the Morriston site.  The department have recruited more Estates Officers; however, we are still out for advert for the fourth time to recruit to existing vacancies which will help address this issue.

## Decontamination

## Decontamination from an AP’s point of view relates to the autoclaves and the ultrasonic

## washers.  These devices are regulated by guidance from the WHTM and there are strict

## rules about the operation of these machines.

## The Decontamination Group is chaired by Infection Prevention and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AP’s, service units and HSDU.

## Key Issues

## Currently the HSDU department in Morriston is being refurbished with activity moved to the Singleton site.  This is presenting operational challenges and the department doesn’t have capacity to meet the Health Boards production demands, and therefore services are currently being supplemented by external contractors.

## The Health Board has completed option appraisals about the centralisation of services.  The Health Board are working with a manufacturer to undertake an efficiency review of the existing services to provide a proposal for how the Health Board can maximise the output by this department.  It is expected this will be completed by the end of the financial year.

- Security

The Health Board has reformed the Security Management Group to act as a focal point for security management issues across the Health Board.  The group is proposed to be a sub-group of the Health & Safety Operational Group.

The Security Group is chaired by the Assistant Director of Estates and meets on a bi-monthly basis.  It is made up of representatives from the two estates departments, service units, Counter Fraud, Health and Safety, Procurement, Capital, Finance, Support Services and the Police.

Key Issues and Mitigation

- Across the Health Board a number of departments have developed Salto security systems.  These are managed differently in different parts of the organisation.  IT colleagues want to develop an access system linked to individuals identification badges and the Health Board needs to consider how

these security systems will be managed holistically across the Health Board.  A working group is being set up to discuss this issue, with the intention of bringing a business case to the Director of Finance and Performance.

- The Health Board is required to undertake a lock down test for its ED departments to ensure the security of these services.  These tests are going to be undertaken over the coming months.

- The Health Board does not have a Security Advisor and these issues are to be identified as potential risks.  A business case is being developed for the Director of Finance and Performance in support of this role.

- The theft of nitrous oxide is becoming a bigger and bigger risk, and control procedures are being reviewed.  Service directorates have been made aware of this issue and additional precautions have been made where appropriate.

- Fire Safety

## The Health Board has completed a review of the fire compartmentation on the Morriston site, and it is intended that this work will be developed into a specification to commission repairs on fire compartmentation on the site.  The 6-Facet Survey has identified a number of issues and the Health Board have had EFAB funding to replace the fire alarm panels on the site.

## The Health Board has already undertaken a review with Arrup to update the compartmentation information.  However, one of the challenges at the moment is that the estates teams are not keeping up with the volume of work that  is being generated by the risk assessments.  Currently out of the team of six carpenters on the Morriston site we only have two working, and likewise in Singleton, nearly 50% of the team are off sick and have been for some time.  As a result, the departments are pulling together some of the risk assessments to develop some specifications to get these works completed by external contractors.  Significant progress has been made in undertaking the fire risk assessment.

The Fire Safety Group is chaired by the Assistant Director of Capital and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE Fire, Health and Safety  and service units.

Fire Dampers

The fire compartmentation reviews will identify the fire dampers, however, a number of them due to their location are inaccessible and therefore unmaintainable as they are often in confined areas or within walls. The 6-Facet survey has provided estimated costs of around £196,000 for the site, excluding fees, contingency and on costs to address the fire damper issues.  As part of the review of fire compartmentation within Morriston the risks associated with the fire dampers have been considered and to be included as part of future capital schemes where appropriate.

Key Issues and Mitigation

- The need for additional staff to carry out work arising from the risk assessments.  The department have seconded a member of staff into a temporary position to pilot a new approach to addressing issues identified within the fire risk assessments.  If successful, a business case will be developed to make this a permanent position.

- The fire alarm service at Morriston Hospital requires replacement.  Funding has been secured through EFAB monies and Capital colleagues have commenced with a two-year programme for its replacement.

- The Health Board would benefit from a Fire Manager, as well as additional Fire Managers, and the Assistant Director for Capital has been supporting the Director of Finance and Performance in the development of a revised structure.

- Waste

The volume of waste produced by the Health Board has increased significantly as a result of the requirement for staff to wear PPE.  The waste whilst not heavy is extremely bulky and the contractor who provides the waste disposal service is now not in a position to cope with this increased demand.   All spare capacity has been lost due to the volume of waste that has been generated.

Contingency arrangements are already in place, however, the sites continue to suffer from delayed collections on a regular basis.  This issue has been escalated through Welsh Government and meetings are being held on a regular basis with the waste disposal company.

Nationally it has been identified that there has been a significant reduction in UK waste storage capacity - due to changes in legislation.  Also, treatment capacity remains finely balanced.  The view from the National Waste Management Group was that capacity will further reduce in the next two years due to impending Statutory Instruments coming into force.  One of which is on site sorting of waste.  We are also being asked to provide refrigeration facilities for the storage of anatomical waste.

The Technical Services Manager is developing an action plan for discussion with the Assistant Director of Estates on how we address known non-conformity issues.

Key Issues and Mitigation

- The Health Board has again been unsuccessful in re-appointing to the position of Technical Services Waste Officer.  The position has been vacant since 2020, during which time we appointed a trainee.  They did apply for the post but took a post with the Council.  This has a direct impact on the service provision compromises the ability to address both audit and legislative requirements.  The department is currently out to advert for this post.

- The Technical Servicers Manager will have to requalify as a COTC holder to back fill this role, as ongoing accreditation is required every two years. No additional resources (staff/capital/ revenue) have been provided to address changes to requirements of increased recycling rates, due to changes in Welsh Government Net Zero requirements 2023 - 25.  The department are putting a proposal together for the Director of Finance and Performance for this function of the department for his consideration.

- Maintenance Services

The Health Board undertakes both reactive and planned maintenance.  The Planned Preventative Maintenance (PPM) is targeted at our statutory obligations.  We try to complete best practice and desirable work as well.  Performance is monitored on a monthly basis, reviewing the scheduled work against that completed.

The following charts show completion of checks by trade for the two main sites.  We also undertake a number of water tests.  These see us complete between 2,500 and 3,000 water tests on each of the main three sites each month.  The following charts identify the number of tasks scheduled against the number of tasks completed.

Whilst compliance is generally good, staff shortages are the key driver for under performance and this is being addressed through an estates wide workforce modernisation programme.

Morriston Year to Date

| Singleton Year to Date |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |

The charts highlight performed generally very good performance, but again, the department affected by sickness absence and vacancies.

Performance against our statutory maintenance tasks is good.  However, our completion of the best practice and on essential tasks suffer as a result.  The

The table below shows the number of outstanding jobs by trade for reactive maintenance.  Sickness within the department, especially a number of long-term issues, are having a profound effect on our performance.  However, the department are targeting as best they can these issues.

| Trade | Less than one week old | 2- to 4-week-old | 1 to 3 months old | Over 6 months old |
| --- | --- | --- | --- | --- |
| Mechanical | 55 | 39 | 69 | 0 |
| Electrical | 39 | 40 | 57 | 0 |
| Carpentry | 0 | 0 | 7 | 15 |
| Semi-skilled | 60 | 61 | 92 | 0 |

- Energy Report

SBU HB Summary – June 2023

Does not include Solar Farm

Degree days:  59 June 2023, (73 June 2018)

Over the last few years, the Health Board has secured significant funding to implement energy reductions and carbon savings.  This has delivered savings over 20% based on our consumption in 2018/19.  However, those savings have been lost due to the changes in service provision through the pandemic in the first instance, and more latterly with the need for services to extend their hours to respond to drives to improve waiting lists.

The department have completed reviews of Singleton and Morriston and have high level proposals to de-steam and decarbonise the Singleton and Morriston sites.  The department has completed 28 energy decarbonising reviews of properties within primary care, as well as commissioned further reviews of Gorseinon, Llwyneryr and Tonna hospitals.  The department has also started conversations with the PFI SPV Baglan Moore Heath Care around how we can develop a decarbonising strategy for the PFI site, linked to the life cycle works required under the contract.  The Chief Executive is writing to the Welsh Government around funding options for these proposals across the Health Board, which total over £60million

- Policies

The department oversees the production of the number of specialist policies.  It has recently updated its Asbestos and its Waste Management policy for the Health Board, both of which have been shared with the Health and Safety Operational Group for comment prior to being presented to this forum for adoption.

- Contractor Control

The department has numerous contracts in place for specialist engineering services.  Internal Audit through their reviews have highlighted issues around three aspects of the management of that process.  The first being confirmation that companies have the appropriate insurance, method statements and risk assessments in place.  To address this the department are working with procurement colleagues to ensure that were appropriate these are requested as part of any quotation process.  To support this the department is also developing its own database of risk assessments, method statements and insurance documentation for the companies it routinely employs.

From previous audits we had identified that some staff, whilst they had signed into site, had not signed off once they had completed the work.  Whilst the last audit didn’t identify any incidents where this was the case, a draft letter for the department has been produced which will be sent to companies that have staff that leave site without signing out.  Within the letters companies advised that should this reoccur; the individual may be restricted to returning to site.

Historically audits have found staff have attended sites on behalf of external contractors but have not always attended induction to the site. This is difficult to police, especially when we have large capital projects ongoing.  The department has undertaken an audit of induction compliance which has identified three companies that had staff attend site who hadn’t undertaken induction.  The Assistant Director of Estates has written to these companies, highlighting this fact, and asking the companies to provide written confirmation that the individuals concerned have read and understood the induction pack – a copy of which was provided.  This approach will aim to improve compliance going forward.

- GOVERNANCE AND RISK ISSUES

The Estates department maintains its own risk register which feeds into the corporate risk register.  The issues identified within this paper, where appropriate, have been added to the estates risk register.

From a governance point of view, each of the sub-groups meet on a regular basis to ensure actions are being taken to address areas of concern.  There are however limitations to the mitigation due to the financial implications of some issues.  The Health Board has submitted its estates strategy to the Welsh Government which provides a clear plan on how the Health Board can address its main backlog maintenance risks.  If funding is not forthcoming risks will continue to be managed through the existing controls.

For added assurance, reports will be routinely submitted to this committee.

Audit action delivery has been challenging but a recent dedicated focus on outstanding audit actions is delivering good progress in action closure. This will be overseen by the Health Board’s Audit Committee but in summary the key issues are: -

MA8.1a and MA8.1b  Water Safety

Training requirements and training matrix to be included in the Water Safety Plan.  This has been actioned.

Internal Audit are awaiting minutes of the last water safety group to confirm this was agreed.  This recommendation will then be able to be closed down.

MA2  Financial Safeguarding

Review and update of health board procedures and SFI/SOs, where appropriate, the Estates department’s requirements for inviting contractors to quote / tender.

The department has been working with Internal audit who are in the process of closing this recommendation as complete.

MA13  Financial Safeguarding

Finalisation and communication of formal procedures for the management of the Estates stores.

The department have been working with Internal Audit and have liaised with them over a draft set of procedures which are due to be submitted by the 18th of August 2023.  Pending Internal Audits agreement this recommendation will then be closed down.

MA14  Financial Safeguarding

Finalisation and communication of the stores practices to reflect audit findings and SFI requirements.

The department have been working with Internal Audit and have liaised with them over a draft set of procedures which are due to be submitted by the 18th of August 2023.  Pending Internal Audits agreement, which will close this item down.

MA2  Control of Contractors

Assurance that contractors have been vetted for appropriate health and safety competency and insurance arrangements prior to appointment.

The department has been working with Internal Audit once again and have provided evidence around the procurement process along with the monitoring of insurances, competencies  and evidence of method statements.  This due to be presented to Internal Audit by the 18th of August 2023 at which time it is hoped this will provide enough evidence to close down this recommendation.

MA5  Control of Contractors

Provision of induction to contractors prior to commencement of work on health board sites, and monitoring compliance of the same.

The department have shared with Internal Audit a copy of the last audit undertaken of induction compliance and shared the procedures that have been put in place to monitor induction.  The department are awaiting for confirmation that this has met the requirements of the recommendation so that this can be closed down.

MA8  Control of Contractors

Monitoring and reporting, to an appropriate forum, of contractor compliance.

The audit that was undertaken will be reported to the Estates Board but has also been included within this report.  On receipt of minutes Internal Audit have advised they will be happy to close this recommendation

MA1  Waste Management

Waste Management Policy to be reviewed to ensure that all key elements of WHTM 07-01guidance, and enhanced information regarding governance and training requirements are incorporated. Waste Management procedures to be reviewed and updated accordingly.

The waste management policy is appended to this document and has been approved by the Health and Safety Operational group, and we are seeking approval by this committee which will close this recommendation.

MA2  Waste Management

Engagement with an appropriate forum to present the benefits of wider awareness recycling training across the health board.

The department has provided evidence in the form of minutes and papers which have been submitted to the Health Board’s Sustainability forum, which Internal Audit are reviewing as evidence to close this recommendation.

MA4  Waste Management

Reporting of the costs/benefits of the introduction of the offensive (tiger stripe) waste stream to an appropriate forum for onward consideration of the matter outside Estates.

The department has provided evidence in the form of minutes and papers which have been submitted to the Health Board’s Sustainability forum, which Internal Audit are reviewing as evidence to close this recommendation.

MA5  Waste Management

Critical review of waste volumes and types across the health board to be presented to an appropriate forum, to identify potential for waste minimisation in line with WHTM 07-01.

The department has provided evidence in the form of minutes and papers which have been submitted to the Health Board’s Sustainability forum, which Internal Audit are reviewing as evidence to close this recommendation.

MA6  Wate Management

Monitoring of recommendations / non-conformities arising from Pre-Acceptance audits.

Following discussions with Internal Audit to close down this recommendation, they wanted the recommendations to be considered and reported to an appropriate forum.  These recommendations have been included within this report and it is hoped that the copy of the report and minutes will close this recommendation.

- FINANCIAL IMPLICATIONS

Whilst the paper in itself does not have any financial implications, the individual issues identified within the report do require additional finance, whether that be revenue or capital.  Individual papers and business cases will be developed for these issues where appropriate.  It is clear the department needs significant capital to address its maintenance back log issues, as well as additional revenue to enhance the current workforce to meet the operational standards.

Revenue Position

The department are currently £373,794 underspent.  However, there are a number of risks associated with this figure.  These include:

Risks

- Utilities - energy price increases/limited funding available in FY

- Utilities implications of additional developments/services

- Cost increases (Transport, Materials and Parts)

- Contract spend increases

- Food waste, recycling/greening costs

- Increase operating hours to address waiting times unfunded

- Contracts at Morriston hospital - potentially  underpaying us

Opportunities

- PFI - De minimus fund account interest never received

- PFI - revised contract management opportunities

- Contracts at Morriston hospital - potentially underpaying us - what evidence do we have to support this

- Future gains through solar farm and energy storage battery

Whilst the department’s financial position appears strong, there is concern about shifts in utility prices, especially along with the fact that over the winter period we tend to have far more maintenance expenditure.

.

- RECOMMENDATION

Members are asked to:

- NOTE the contents of the report

| Governance and Assurance |  |  |  |
| --- | --- | --- | --- |
| Link to Enabling Objectives (please choose) | Supporting better health and wellbeing by actively promoting and empowering people to live well in resilient communities |  |  |
|  | Partnerships for Improving Health and Wellbeing |  | ☒ |
|  | Co-Production and Health Literacy |  | ☐ |
|  | Digitally Enabled Health and Wellbeing |  | ☐ |
|  | Deliver better care through excellent health and care services achieving the outcomes that matter most to people |  |  |
|  | Best Value Outcomes and High-Quality Care |  | ☒ |
|  | Partnerships for Care |  | ☐ |
|  | Excellent Staff |  | ☐ |
|  | Digitally Enabled Care |  | ☐ |
|  | Outstanding Research, Innovation, Education and Learning |  | ☐ |
| Health and Care Standards |  |  |  |
| (please choose) | Staying Healthy |  | ☐ |
|  | Safe Care |  | ☐ |
|  | Effective Care |  | ☐ |
|  | Dignified Care |  | ☐ |
|  | Timely Care |  | ☐ |
|  | Individual Care |  | ☐ |
|  | Staff and Resources |  | ☒ |
| Quality, Safety and Patient Experience |  |  |  |
| The condition of the estate can have a profound effect on patient experience. Numerous papers extoll the virtue of the impact of the environment a patient is in and the benefits to recovery. Across the functions of the estate, the department has developed clear governance arrangements to ensure risks are identified and plans are put in place to manage these appropriately. It has to be noted that a number of these issues require funding - whether it be capital or revenue, to fully address. Where this is the case, business cases have been prepared and/or have been included within the Health Boards estates strategy. |  |  |  |
| Financial Implications |  |  |  |
| Whilst the paper in itself does not have any financial implications, the individual issues identified within the report do require additional finance, whether that be revenue or capital. Individual papers and business cases will be developed for these issues where appropriate. It is clear the department needs significant capital to address its maintenance back log issues, as well as additional revenue to enhance the current workforce to meet the operational standards. |  |  |  |
| Legal Implications (including equality and diversity assessment) |  |  |  |
| None |  |  |  |
| Staffing Implications |  |  |  |
| The department has identified the need for additional resources and is currently working through a restructuring of the department. This will see the introduction of new roles within the structure, as well as the remodelling of the estates services. The department is currently structured to deliver statutory maintenance only, and work is ongoing to review staffing levels as a result of the clinical services changes being undertaken across the estate. |  |  |  |
| Long Term Implications (including the impact of the Well-being of Future Generations (Wales) Act 2015) |  |  |  |
| n/a |  |  |  |
| Report History |  | Previously routinely reported to the Health and Safety Committee |  |
| Appendices |  | None |  |