`

| Meeting Date | 25th June 2024 |  | Agenda Item |  | 5.1 |
| --- | --- | --- | --- | --- | --- |
| Report Title | Estates Assurance Report |  |  |  |  |
| Report Author | Des Keighan, Assistant Director of Estates |  |  |  |  |
| Report Sponsor | Darren Griffiths, Executive Director of Finance & Performance, Acting Deputy Chief Executive |  |  |  |  |
| Presented by | Des Keighan, Assistant Director of Estates |  |  |  |  |
| Freedom of Information | Open |  |  |  |  |
| Purpose of the Report | The purpose of this report is to provide an update on the range of activities undertaken in respect of the management of the Health Board’s estate. |  |  |  |  |
| Key Issues | The report provides an update on key operational matters relating to the management of the Health Board’s estate. The key areas covered in this report are: - - Backlog maintenance - Asbestos management - Water safety - Medical gas pipeline systems - Electrical services - Ventilation systems - Decontamination - Security - Fire safety - Waste management - Maintenance services - Energy - Audit Statistical analysis for elements of estates performance have been included and will be developed in future reports to meet the needs of the Committee. |  |  |  |  |
| Specific Action Required (please choose one only) | Information | Discussion | Assurance | Approval |  |
|  | ☒ | ☐ | ☒ | ☐ |  |
| Recommendations | Members are asked to: - NOTE the report |  |  |  |  |

ESTATES ASSURANCE REPORT

- INTRODUCTION

The purpose of this report is to provide an update on the range of activities undertaken in respect of the management of the Health Board’s estate.   Due to the nature of some of the infrastructure challenges across the estate, progress has not been possible without capital investment.  The Health Board has developed its Estates Strategy which maps out its plans for the estate.  This report provides an update on the provision of existing services. The report contains a considerable amount of detail, however, as requested some statistical analysis of estates performance has been included and it is recognised that the report will need to evolve to develop data which meets the needs of the Committee.

- BACKGROUND

This section of the report provides an update across all the key areas of work undertaken by the estates team.

- Backlog maintenance

As previously reported, the Health Board has undertaken a six-facet survey of its entire estate to provide a benchmark for its services.  The Health Board has commissioned a 20% review of its Estate.  Which was completed at the end of April the result is that our back log figure has increased to £130,042,891. This reassessment of 20% of the Health Board’s floor area focused on the main Hospital sites and looked at the risks that were at the top of their individual categories to see if they had moved into a higher category of risk.

The assessment revisited the cost associated with the backlog across the whole of the Estate, based on the latest cost schedules.  The current backlog figure is based on having an Estate which is to have the physical Estate in Condition B.  Condition B requires little or minor upgrading.  From this review the Health Board has identified a cost increase of non-risk adjusted of over £8 million to bring the estate up to Condition B, over a range of services which are summarised in the table below.

2023 /2024

| Row Labels | HIGH | LOW | MODERATE | SIGNIFICANT | Grand Total |
| --- | --- | --- | --- | --- | --- |
| Cefn Coed Hospital |  | 677650 | 2891200 | 2947750 | 6516600 |
| Gorseinon Hospital |  | 530500 | 2450300 | 1009600 | 3990400 |
| Morriston Hospital | 5862000 | 5533980 | 21585350 | 22211430 | 55192760 |
| Singleton Hospital | 3095000 | 4468500 | 20546750 | 21558260 | 49668510 |
| Tonna Hospital | 100000 | 587750 | 938800 | 3899770 | 5526320 |
| Grand Total | 9247950 | 13516830 | 49875805 | 53006290 | 125646875 |

2024 / 2025

|  | HIGH | LOW | MODERATE | SIGNIFICANT | Grand Total |
| --- | --- | --- | --- | --- | --- |
| Cefn Coed Hospital |  | 704,078 | 3,003,957 | 3,062,712 | 6,770,747 |
| Gorseinon Hospital | 116,500 | 144,500 | 2,026,000 | 2,424,600 | 4,711,600 |
| Morriston Hospital | 6,755,918 | 5,628,744 | 21,269,138 | 25,165,932 | 58,819,731 |
| Neath Port Talbot Hospital |  | 594,412 | 225,463 | 276,842 | 1,096,716 |
| Singleton Hospital | 3,240,705 | 4,205,845 | 23,427,789 | 26,177,272 | 57,051,610 |
| Tonna Hospital | 23,000 | 198,500 | 271,250 | 4,802,270 | 5,295,020 |
| Grand Total | 10,136,123.00 | 11,476,078.27 | 50,223,596.50 | 61,909,627.46 | 133,745,425.23 |

These costs are the raw costs to carry out the work and do not include overheads, fees or any enabling works.  The costs above are only for the main hospital sites work is ongoing on updating on costs across the health board with the latest industry standards it has to be recognised however the costs indicated above are to complete the work alone and do not include decant costs, professional fees or any on costs therefore, costs can vary by up to 120%.

- Estates maintenance

The estates function has a duty to ensure that engineering services are maintained in accordance with both Legislation and with the Hospital Technical Memorandum (HTM), which are effectively the industry guidelines.  The Health Board has identified a number of key elements that have to be managed as specialist functions. These are: -

- Asbestos

- Water

- Medical gases

- High voltage and low voltage electricity

- Ventilation

- Decontamination

- Security

- Fire

- RAAC

For each of these specialities the Health Board has subgroups which have been established to ensure that the Health Board discharges its duties in these areas.

A number of these services require the appointment of a designated person for all estates issues, which is the Director of Finance and Performance, and a Senior Operational Manager (SOM) who takes professional responsibility of the estate, with this role being undertaken by the Assistant Director of Estates.  The Assistant Director of Estates is supported by Authorised Persons (AP’s) who have attended appropriate training, have been independently assessed and appointed in writing, to undertake these duties for specific functions of the estate.  Currently one of the key issues, due to lack of staff, is an inability to recruit to a number of positions, and as a result of guidance on how many of these AP duties an individual can take, we have insufficient AP’s for specific disciplines on the Morriston site. Detailed below is the current status on each of these specialities.   Terms of reference are available for all of the groups should the Committee wish to have sight of these.

- Asbestos Management

The Health Board is undertaking reviews of the asbestos management plans, which are updated on an annual basis.  Within last financial year, we completed projects through the Estates Funding Advisory Board (EFAB) scheme which have addressed issues in the roof void within Philips Parade and an area of underground duct beneath Ward 1 in Singleton Hospital. For this financial year, the Health Board has been successful in securing £200,000 worth of investment and we have now developed an Action Plan which will continue to focus on the Singleton Hospital site.

For asbestos management there is a sub-group of the Health and Safety Operational Group that meets on a quarterly basis, with representatives from the two estates departments, Health and Safety and the Estates Health and Safety Officer.

Key Issues and Mitigation

- Singleton Hospital presents the most challenges due to the number of areas that are affected by the presence of asbestos.  Whilst we have clear protocols to mitigate any risk, the presence of asbestos in the voids present significant operational difficulties.  Simple blockages cannot be addressed by the estates staff but require the attendance of specialist contractors licenced to work within these areas.  All voids within the Singleton site have restricted access due to the presence of asbestos.

- Another significant area of concern is the asbestos in the risers. Within the main hospital blocks the main drainage stacks come down through the building. These rises in the Moscow cases have asbestos within them if we get an issue on the stack itself which means that it has a leak this could result in areas of the hospital being not serviceable due to a lack of access to these areas so we are trying to target these voids as a priority

- Water

The Health Board will be looking to tender for the provision of water management risk assessments this financial year, as the last ones were completed in 2022.     This year the priorities have been identified as Outpatients in Singleton Hospital and Cimla Hospital and the work will be completed by the end of the financial year. The Health Board’s Water Management group is chaired by the Director of Performance and Finance and meets on a quarterly basis.  It is made up of representatives from the two estates departments, Authorising Engineer (AE) Water, service units, Infection Prevention, Capital, as well as Authorised Persons (AP’s) from each site.

Key Issues and Mitigation

- Welsh Water have visited both the Morriston and Singleton site and have issued a list of remedial works they require undertaking.  Both sites are working through these documents.  As part of the department’s mitigation of this issue, a bid for capital funding Was meant for this financial year which was successful and we secured additional funding for this financial year the two estates departments are developing their plans based on the funding available.

- There have been a number of issues associated with pseudomonas with testing through recent months.  Following the Water Safety Committee we have constituted a Task & Finish Group to revisit the areas that need to be tested for pseudomonas and the frequency of the testing.  The task and finish groups have identified those areas which need now to have regular pseudomonas testing in accordance with the Welsh Health Technical Memorandum. However, this has an additional resource implication with regards staffing requirements to undertake this additional testing which has been captured within the review of workforce requirements for the two sites. These requirements are captured later in this document.

- There are now both AP’s in place at Singleton and Morriston, however, an Authorised Person is required for the Morriston site.  An individual has been identified and training has been planned.  Cover is being provided on a temporary basis by the former Morriston Estates Manager who has now taken a central role within the department.

- Medical Gas Pipeline Systems

The Medical Gas Group meets on a quarterly basis.  It is made up of representatives from the two estates departments, service units, Pharmacy, Support Services, Quality Control Pharmacist, midwifery, theatres, as well as the AP’s from each site.

The Health Board has AP’s appointed on both sites; however, an AP is still required on the Morriston site.

Key Issues and Mitigation

- The removal of nitrous oxide piped medical gas systems – a trial has commenced on the Singleton Hospital site and now the Morriston site and its money in the next few months we will be in a position to move away from a piped nitrous oxide system on the two sites.

- The Health Board is considering a training programme for the designated nursing officers but on researching this issue it's been decided that this needs to be outsourced because the courses have to be provided by specialist providers. An options paper is being developed on the way forward for the interim director of Capital and Estates

- The programme that has been developed for training our staff on medical gases has been the subject of national awards and the work done by the ABM E departments has been recognised and adopted by a number of organisations not just within Wales but across the UK.

- Electrical Services – High (HV) and Low Voltage (LV)

There are issues on both sites with regards to electrical services and their compliance with the Welsh Health Technical Memorandums (WHTM’s).  A number of the systems, by nature of their design and age, do not comply with latest guidance.  There are loading issues on the Morriston site, however it is hoped that the work being completed on Sub Station 6 (a development approved by the Health Board and funded by Welsh Government (WG)) will help to address this issue.

As part of the 6-Facet review £12.8million of cost was identified to upgrade and renew the existing electrical systems across the Health Board.  These works were part of the submission to Welsh Government as part of the estates strategy approved by the Board.  The Electrical Group is chaired by the Assistant Director of Estates and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE’s for HV and LV and Capital.

Key Issues and Mitigation

- There has been an increase in the number of AP’s on the Morriston Hospital site.

- Remedial works on Sub 2.  This has been allocated capital to address some of the issues and the works Are nearing completion this financial year.

- Sub 6 development.  This is currently being overseen by Capital colleagues and is due to be completed shortly.

- Ventilation Systems

The last Audit Report highlighted the fact that a large proportion of our plant is non-compliant with the current WHTM’s, noting that the plant was not designed to meet the current standards.  These shortcomings have been highlighted in the Estates strategy which has now been approved by the Board.  The Chief Executive Officer and Director of Finance and Performance have now presented the Estates Strategy to the Welsh Government for their consideration.  This outlines the capital required to deliver the changes required. We have been securing successful further capital from the Efab funding stream to address air conditioning issues on the two main sites. capital we will be refurbishing the air conditioning units on some of the theatres on the Singleton site

The Ventilation Group is chaired by the Assistant Director of Estates and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE Vent, Capital and Health and safety.

Key Issues and Mitigation

- Throughout the Morriston site, the ward areas ventilation systems were not designed to deliver the air change rates recommended since the pandemic.  Their design is predicated on providing air changes to the core areas which is supplemented by opening windows.  This has been recognised within the backlog maintenance costs developed under the 6-Facet survey.  This forms part of the plans detailed within the Estates Strategy which has been shared with the Welsh Government, seeking funding of over £840 million to address backlog maintenance issues.

- The Health Board has secured £680K for this year which will be used to address issues on both the Singleton and Morriston Hospital sites.

- Lack of sufficient AP’s on the Morriston site.  A member of staff now attended the AP training and he's waiting assessment by the AE.

## Decontamination

## Decontamination from an AP’s point of view relates to the autoclaves and the ultrasonic washers.  These devices are regulated by guidance from the WHTM and there are strict rules about the operation of these machines.

## The Decontamination Group is chaired by Infection Prevention and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AP’s, service units and HSDU.

## Key Issues and Mitigation

## The Health Board has completed option appraisals about the centralisation of services.  The Health Board is working with a manufacturer to undertake an efficiency review of the existing services to provide a proposal for how the Health Board can maximise the output by this department.  At the same time the Health Board has contacted neighbouring Health Boards to discuss the development of a shared facility, however, this has not progressed.

## The health board is starting discussions with other health boards along the M4 corridor about a central HD facility and looking at options appraisals of the provision of a centralised HSD you for the health board itself.

- Security

The Health Board has reformed the Security Management Group to act as a focal point for security management issues across the Health Board.  The group is proposed to be a sub-group of the Health & Safety Operational Group.

The Security Group is chaired by the Assistant Director of Estates and meets on a bi-monthly basis.  It is made up of representatives from the two estates departments, service units, Counter Fraud, Health and Safety, Procurement, Capital, Finance, Support Services and the Police.   The lockdown exercise at Morriston Hospital identified a number of issues that need to be addressed both with regard to the physical access to the site at night.  The Site Management Teams have reviewed their lockdown procedures for the main sites.

Key Issues and Mitigation

- A working group is being set up to discuss the Salto locking systems with the intention of bringing a business case to the Director of Finance and Performance which is still ongoing.  The Health Board has met with the Salto system manufacturers to discuss how it can more effectively manage the system.  Meetings are planned in April to take this forward.

- The Health Board does not have a Security Advisor and these issues are to be identified as potential risks.  A business case is being developed for the Director of Finance and Performance in support of this role.

- Following discussions between the Acting Deputy Chief Executive and the Chief Operating Officer around their portfolios, the chairing of the security committee has passed to the head of support services.

- Fire Safety

## The Health Board has completed a review of the fire compartmentation on the Morriston site, and it is intended that this work will be developed into a specification to commission repairs on fire compartmentation on the site.  The 6-Facet Survey has identified a number of issues and the Health Board have had EFAB funding to replace the fire alarm panels on the site.

## The Health Board has already undertaken a review with Arrup to update the compartmentation information.  However, one of the challenges at the moment is that the estates teams are not keeping up with the volume of work that is being generated by the risk assessments.   The department still have problems with staffing numbers due to sickness, however, the department has been undertaking work analysis that show that we require additional staff in a number of disciplines.

## Capital colleagues have helped develop specifications for some of the fire compartmentation work on the Morriston site. The Fire Safety Group is chaired by the Assistant Director of Capital and meets on a quarterly basis.  It is made up of representatives from the two estates departments, AE Fire, Health and Safety and service units.

Fire Dampers

The fire compartmentation reviews will identify the fire dampers, however, a number of them due to their location are inaccessible and therefore unmaintainable as they are often in confined areas or within walls. The 6-Facet survey has provided estimated costs of around £196,000 for the site, excluding fees, contingency and on costs to address the fire damper issues.  As part of the review of fire compartmentation within Morriston the risks associated with the fire dampers have been considered and to be included as part of future capital schemes where appropriate.

Key Issues and Mitigation

- Capital colleagues have helped develop specifications for the fire compartmentation and fire risk assessments in a few areas, however, further significant investment is still required.

- The fire alarm service at Morriston Hospital is now being replaced as funding was secured through EFAB monies and Capital colleagues are progressing tear two of a two-year programme for its replacement.

- The Health Board would benefit from a Fire Manager, as well as additional Fire Officers, and the Assistant Director for Capital has been supporting the Director of Finance and Performance in the development of a revised structure.

- Reinforced Autoclave Aerated Concrete (RAAC)

The Health Board was required to undertake a review of all its properties within its ownership including secondary, primary and community properties for the presence of RAAC.  It did not include our PFI hospital as this was constructed outside the period identified.  With regards to the leased properties, Capital colleagues have written to all landlords in March of this year asking for confirmation from them that they have undertaken an appropriate RAAC review.  We have now had confirmation that these properties are free from RAAC.

In November 2023, Welsh Government asked Health Boards to review properties from which it delivered services which were outside its ownership.  We have now written to all 84 property owners and of the 84 properties we have had confirmation from 72 of these properties that RAAC is not present within their buildings. This has been based on either a Structural Engineer’s report, confirmation from the Landlord, or as a result of the fact the property was constructed outside the time frame identified as being at risk of containing RAAC.

Of the 12 properties outstanding, 11 of these buildings are operated by Boots the Chemist, who have advised that they are prioritising their surveying schedule based on the age of the properties. They identified 3 levels of risk, Priority 1 properties are defined as those which were constructed between 1950 and 1962, Priority 2 properties are defined as ones constructed between 1963 and 1991 and Priority 3 properties being defined as ones constructed between 1992 and 2011.

The Health Board does not operate its services within any Priority 1 building.   We have written back to Boots the Chemist asking for an expected timeline for when the rest of the surveys will be completed.

- Waste

The volume of waste produced by the Health Board has increased significantly as a result of the requirement for staff to wear PPE.  The waste whilst not heavy is extremely bulky and the contractor who provides the waste disposal service is now not in a position to cope with this increased demand.   All spare capacity has been lost due to the volume of waste that has been generated.

Contingency arrangements are already in place, however, the sites continue to suffer from delayed collections on a regular basis.  In the last quarter we have continued to experience significant problems with services.  This issue has been escalated through Welsh Government again and meetings are being held on a regular basis with the waste disposal company.

Nationally it has been identified that there has been a significant reduction in UK waste storage capacity - due to changes in legislation.  Also, treatment capacity remains finely balanced.  The view from the National Waste Management Group was that capacity will further reduce in the next two years due to impending Statutory Instruments coming into force.  One of which is on site sorting of waste.  We are also being asked to provide refrigeration facilities for the storage of anatomical waste.

The Technical Services Manager is developing an action plan for discussion with the Assistant Director of Estates on how we address known non-conformity issues.

Key Issues and Mitigation

- The Health Board was successful in re-appointing to the position of Technical Services Waste Officer but unfortunately, the individual declined the offer of appointment and the department are looking at different options on how we could cover the post as a development opportunity.

- The Technical Servicers Manager has now requalified as a COTC holder to back fill this role, as ongoing accreditation is required every two years. No additional resources (staff/capital/ revenue) have been provided to address changes to requirements of increased recycling rates, due to changes in Welsh Government Net Zero requirements 2023 - 25.  There is new legislation on the recycling of waste streams which has put the responsibility on the Health Board to provide additional waste stream.  A proposal is being developed and has been already shared with the Sustainability Group identifying budget costs which will then be fed into the Quality & Assurance Committee.

- New legislation is coming to play around recycling the health board committed to the appointment of additional auditing staff and bins through its community services to ensure compliance with the new legislation this process will be ongoing over the coming months as an the additional equipment is purchased and stuff put into place.

- Maintenance Services

The Health Board undertakes both reactive and planned maintenance.  The Planned Preventative Maintenance (PPM) is targeted at our statutory obligations.  Performance is monitored on a monthly basis, reviewing the scheduled work against that completed.     The tables overleaf captures the department’s performance over a range of its services.  It shows the number of statutory maintenance checks which were due to be completed against the numbers completed.

Whilst performance has suffered recently as can been seen in the KPI table in Appendix 1 this can be linked to the sickness absence levels in the department. The department has been consulting on changes have following consultation been implemented which has affected working practises that have affected the shift patterns in place. These changes have adversely affected staff pay although they are receiving protection, the changes bring them in line with working practices within the rest of the health board however this is resulting in a loss of goodwill from staff. The department are currently reviewing the Planned Preventative Maintenance Programme to ensure the prioritisation of work.

The current approach prioritises the completion of Statutory Maintenance above reactive breakdowns which leads to criticism on occasions, however, this is linked to the workforce review we are currently undertaking. The department historically has compiled a number of papers that identified the need for additional resources. A review of the planned maintenance and reactive maintenance has shown we need the following additional staff across the two departments.

Staffing Levels

|  | Morriston |  |  | Singleton |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Trade | Establishment | Required | Establishment |  |  | Required |
| Carpenter | 6 | 9 | 6 |  | 8 |  |
| Electrical | 11 | 12 | 8 |  | 8 |  |
| Mechanical | 13 | 14 | 7 |  | 10 |  |
| Semi-skilled | 17 | 23 | 15 |  | 18 |  |
| Wet | 1 | 1 | 2 |  | 1 |  |

* The figures do not take into consideration the extension of services on the site.

It’s important to note that within the current establishment there are a number of vacancies.  The department is using agency staff and there are staff currently transitioning through Trac to become permanent members of staff.  We need not just to fill the current vacancies, but to meet the required establishments if we are to improve services and meet the current service demand. The department does not have sufficient resources. As a result, we have prioritised completion of the statutory maintenance, whilst the current completion levels were good, the introduction of shift changes has adversely impacted this performance.

Our reactive maintenance performance is currently a real issue and is facing a number of challenges which can be linked to the introduction of the revised working patterns and high levels of sickness within the department. At this point in time, the high sickness levels are adversely affecting the department. This makes it extremely difficult to deliver a service that matches service users’ expectations. Consideration is being made as to how to support staff to return to work.

Estates Management

Welsh Health Shared Services provide authorised engineer (AE) services to the health board.  The role of the authorised engineer is to provide the designated person with independent advice and guidance on the management of these specialist engineering services.  The AE audits these services, within the audit they make recommendations on how the services’ management can be improved.  They can also recommend the number of Authorised Persons for each discipline within the audit. It's important to note that guidance states that each officer should only undertake two AP duties. Whilst Estates Managers, Shared Services and their deputies can be AP’s, it has to be recognised that their duties will make it difficult for them to fulfil this role for each site.

Morriston

The function currently has five engineering Estates Officers, one Building Officer and the Operational Manager and Estates Manager in Morriston. The building officer however would not normally be expected to undertake engineering AP duties.

Also, whilst it is reasonable to expect the estates manager to hold AP duties based on their role within the department, they would not normally have the capacity to undertake these duties on a routine basis. Therefore, ideally, they should be trained as AP but not expected to undertake these duties on a day-to-day basis.

It is also important to note that the Shared Services do not provide authorised engineered services for lifts. However, we need to appoint Authorised Persons but have no way currently of doing so. The management team are currently trying to get costs to provide AE services however, we have appointed a competent lift company to act as that AP for lifts, therefore we need to consider how those roles will be undertaken.

This gives us 6 officers which allows us to provide a maximum of 12 AP duties. From the audits we would require 9 officers to undertake the AP duties required by the site and this is before supporting Capital projects. This would mean that we need 3 further Estates Officers within the Morriston site.

Singleton

For the Singleton site they have recommended a total of 14 AP duties. Currently there are six staff, four estates officers, the operational maintenance manager and the estates manager on the Singleton site. This means we would need an additional estates officer on that site to provide the level of cover required.

The team is starting a process of restructuring within the capital and estates function and recognises the need to enhance the provision of services across the estate these issues will be taken into consideration as part of this process.

A review of the workload has identified the need for both carpentry staff and semi-skilled staff.  There are requests to increase the level of pseudomonas testing across the main sites.  Initial calculations are showing that this would require 10/12 semi-skilled staff and 6/7 carpentry staff across the two sites.

There has also been a request to increase the level of painting carried out.  Currently we have 6 painters on each site and unfortunately a number of those staff are off sick.  Originally we were working on the premise there would be a Capital Painting Programme to support the estates staff, however funding has not always been available.

- Energy Report

| Health Board Summary | Gas | Electricity |
| --- | --- | --- |
| Actual 2023 / 2024 | 49,831,098 | 21,976,391 |
| Target 2023 / 2024 | 51,369,155 | 22,934,363 |
| Saving (kWh) | 1,538,057 | 957,972 |
| Solar Farm |  |  |
| Produce for our use (kWh) |  | 3,248,710 |
| Exported (kWh) |  | 396,940 |
|  | Gas | Electricity |
| Total Saving kWh | 1,538,057 | 4,603,622 |
| Total Saving £ | £153,806 | £1,413,662 |

Performance for both utilities over achieved on the performance targets, saving over 957,000 kilowatts of electricity across the estate and over 1.5 million kWh gas. The solar farm produced 3.2 million kWh of electricity which was used by Morriston Hospital and exported over 396,000 kW to the grid. This produced savings of one and a half £1,500,000 last year for the Health Board. However, the continued development of services is putting greater demands on the electrical consumption, as services extend their operational hours.

We are working with Swansea University MSc marketing students and data analyst students to try and develop energy awareness campaigns that are more “user friendly” and are looking at how we can present energy data in a more dynamic and informative way, utilising different forms of media.  The successful completion of the expansion of the solar farm and the installation of the battery should further enhance the savings that we're able to achieve.

The department has also started conversations with the PFI SPV Baglan Moore Heath Care around how we can develop a decarbonising strategy for the PFI site, linked to the life cycle works required under the contract.  The Chief Executive has written to  Welsh Government around funding options for these proposals across the Health Board, which total over £60million. Whilst the reply recognised all the good work the Health Board had completed, it did not advise as to what funding streams were available.

The department are working with local partnerships (a Government Agency) looking at how we could access new funding routes by adopting the new Re:Fit contract with our current contractor, which allows them as part of the contract to access private finance.

- Policies

The department oversees the production of the number of specialist policies.  No new policies have been re approved in the last quarter

- Contractor Control

The department has numerous contracts in place for specialist engineering services.  Internal Audit through their reviews have highlighted issues around aspects of the management of that process.  The first being confirmation that companies have the appropriate insurance, method statements and risk assessments in place.  To address this the department are working with procurement colleagues to ensure that were appropriate these are requested as part of any quotation process.  To support this the department is also developing its own database of risk assessments, method statements and insurance documentation for the companies it routinely employs.

From previous audits we had identified that some staff, whilst they had signed into site, had not signed off once they had completed the work.  Whilst the last audit didn’t identify any incidents where this was the case, a draft letter for the department has been produced which will be sent to companies that have staff that leave site without signing out.  Within the letters companies advised that should this reoccur; the individual may be restricted to returning to site.

Statistics on the outcome of the audits was included within the information in appendix 1.

- GOVERNANCE AND RISK ISSUES

The Estates department maintains its own risk register which feeds into the corporate risk register.  The issues identified within this paper, where appropriate, have been added to the estates risk register.

From a governance point of view, each of the sub-groups meet on a regular basis to ensure actions are being taken to address areas of concern.  There are however limitations to the mitigation due to the financial implications of some issues.  The Health Board has submitted its estates strategy to the Welsh Government which provides a clear plan on how the Health Board can address its main backlog maintenance risks.  If funding is not forthcoming risks will continue to be managed through the existing controls.

For added assurance, reports will be routinely submitted to this committee.

Audit action delivery has been challenging but a recent dedicated focus on outstanding audit actions is delivering good progress in action closure. This will be overseen by the Health Board’s Audit Committee but in summary the only remaining issue currently is: -

MA6  Waste Management

Monitoring of recommendations / non-conformities arising from Pre-Acceptance audits.

There is still further work to do around the monitoring of pre-acceptance audits and it is hoped with the appointment of the new Waste Officer would have resolved this but as we failed to recruit we are looking at offering this post as a development opportunity.

- FINANCIAL IMPLICATIONS

Whilst the paper in itself does not have any financial implications, the individual issues identified within the report do require additional finance, whether that be revenue or capital.  Individual papers and business cases will be developed for these issues where appropriate.  It is clear the department needs significant capital to address its maintenance back log issues, as well as additional revenue to enhance the current workforce to meet the operational standards.

Revenue Position

The department is currently overspent.  However, there are a number of risks associated with this figure.  These include:

Pay £111k overspend

Estates - £68k under due to vacancies (inc new investments) offset by agency staff

Non pay £306k overspend

- £126k monthly Run Rate Reduction pressure

- £123k pressures in Energy-Work being carried out to look into this

- £93k in building contracts and materials

- £20k benefit in Waste and £15k in systems

Risks

- Utilities - energy price increases/limited funding available in FY

- Utilities implications of additional developments/services

- Cost increases (Transport, Materials and Parts)

- Contract spend increases

- Food waste, recycling/greening costs

- Increase operating hours to address waiting times unfunded

- Contracts at Morriston hospital - potentially  underpaying us

Opportunities

- Previously we had identified that we were pursuing the interest from the de minimus fund linked to the PFI this has now been agreed and the health board will receive £137,000 in settlement,

- Department close to agreeing a settlement figure for performance issues on the PFI contract this is in the sum of £250,000

- PFI - revised contract management opportunities

- Contracts at Morriston hospital - potentially underpaying us - what evidence do we have to support this

- Future gains through solar farm and energy storage battery

- savings from the changes to shift well Ann coming to play falling the protection period of 12 months.

Whilst the department’s financial position is currently overspent the department is working hard to identify further savings however rising costs for materials and parts is put into the pressure on the department.

.

- RECOMMENDATION

Members are asked to:

- NOTE the contents of the report

| Governance and Assurance |  |  |  |
| --- | --- | --- | --- |
| Link to Enabling Objectives (please choose) | Supporting better health and wellbeing by actively promoting and empowering people to live well in resilient communities |  |  |
|  | Partnerships for Improving Health and Wellbeing |  | ☒ |
|  | Co-Production and Health Literacy |  | ☐ |
|  | Digitally Enabled Health and Wellbeing |  | ☐ |
|  | Deliver better care through excellent health and care services achieving the outcomes that matter most to people |  |  |
|  | Best Value Outcomes and High-Quality Care |  | ☒ |
|  | Partnerships for Care |  | ☐ |
|  | Excellent Staff |  | ☐ |
|  | Digitally Enabled Care |  | ☐ |
|  | Outstanding Research, Innovation, Education and Learning |  | ☐ |
| Health and Care Standards |  |  |  |
| (please choose) | Staying Healthy |  | ☐ |
|  | Safe Care |  | ☐ |
|  | Effective Care |  | ☐ |
|  | Dignified Care |  | ☐ |
|  | Timely Care |  | ☐ |
|  | Individual Care |  | ☐ |
|  | Staff and Resources |  | ☒ |
| Quality, Safety and Patient Experience |  |  |  |
| The condition of the estate can have a profound effect on patient experience. Numerous papers extoll the virtue of the impact of the environment a patient is in and the benefits to recovery. Across the functions of the estate, the department has developed clear governance arrangements to ensure risks are identified and plans are put in place to manage these appropriately. It has to be noted that a number of these issues require funding - whether it be capital or revenue, to fully address. Where this is the case, business cases have been prepared and/or have been included within the Health Boards estates strategy. |  |  |  |
| Financial Implications |  |  |  |
| Whilst the paper in itself does not have any financial implications, the individual issues identified within the report do require additional finance, whether that be revenue or capital. Individual papers and business cases will be developed for these issues where appropriate. It is clear the department needs significant capital to address its maintenance back log issues, as well as additional revenue to enhance the current workforce to meet the operational standards. |  |  |  |
| Legal Implications (including equality and diversity assessment) |  |  |  |
| None |  |  |  |
| Staffing Implications |  |  |  |
| The department has identified the need for additional resources and is currently working through a restructuring of the department. This will see the introduction of new roles within the structure, as well as the remodelling of the estates services. The department is currently structured to deliver statutory maintenance only, and work is ongoing to review staffing levels as a result of the clinical services changes being undertaken across the estate. |  |  |  |
| Long Term Implications (including the impact of the Well-being of Future Generations (Wales) Act 2015) |  |  |  |
| n/a |  |  |  |
| Report History |  | Previously routinely reported to the Health and Safety Committee |  |
| Appendices |  | None |  |

| 85% - 100% | Appendix 1: Estates KPI Dashboard - Health Board |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 75% - 84% |  |  |  |  |  |  |  |  |  |  |
| < 75% |  |  |  |  |  |  |  |  |  |  |
|  | Lagging Indicators | Frequency 2023/24 |  |  |  |  |  |  |  |  |
| KPI Groups | Measures | Q1 Target | Q1 Actual | Q2 Target | Q2 Actual | Q3 Target | Q3 Actual | Q4 Target | Q4 Actual | Status |
| Electrical (LV) | Measures | Q1 Target | Q1 Actual | Q2 Target | Q2 Actual | Q3 Target | Q3 Actual | Q4 Target | Q4 Actual | Status |
|  | Monthly checks (insert no: overall) | 224 | 223 | 217 | 183 | 263 | 255 | 233 |  |  |
|  | Quartely Checks | 13 | 13 | 7 | 6 | 13 | 12 | 16 |  |  |
|  | Yearly checks | 70 | 69 | 61 | 50 | 53 | 47 | 14 |  |  |
| Ventilation | Measures | Q1 Target | Q1 Actual | Q2 Target | Q2 Actual | Q3 Target | Q3 Actual | Q4 Target | Q4 Actual | Status |
|  | Monthly checks (insert no: overall) | 317 | 314 | 346 | 335 | 116 | 86 | 349 |  |  |
|  | Quartely Checks | 44 | 41 | 40 | 37 | 30 | 28 | 56 |  |  |
|  | Yearly checks | 98 | 94 | 138 | 134 | 43 | 15 | 21 |  |  |
| Water Safety Assessments | Measures | Q1 Target | Q1 Actual | Q2 Target | Q2 Actual | Q3 Target | Q3 Actual | Q4 Target | Q4 Actual | Status |
|  | Risk Assessments complete | 2022 |  |  |  |  |  |  |  |  |
|  | Action Plans in place |  | yes |  |  |  |  |  |  |  |
|  | Flushing Systems/checks in place | yes | yes |  |  |  |  |  |  |  |
|  | Appointed Persons in place | Yes | Yes |  |  |  |  |  |  |  |
|  | Number of AP's: | (3) | (3) |  |  |  |  |  |  |  |
| Waste Management | Measures ( Tonnage) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | Status |
|  | Combustion | 1326 |  |  |  |  |  |  |  |  |
|  | Food | 21 |  |  |  |  |  |  |  |  |
|  | Recycling | 631 |  |  |  |  |  |  |  |  |
|  | Infectious waste | 1635 |  |  |  |  |  |  |  |  |
|  | High Temp Incieration | 268 |  |  |  |  |  |  |  |  |
|  | ISO 14001 accreditation audit | x | x |  |  |  |  |  |  |  |
|  | Action plan in place | X | X |  |  |  |  |  |  |  |
| Security | Measures | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | Status |
|  | Buidling security assessment in place | yes |  |  |  |  |  |  |  |  |
|  | Lockdown process in place/tested | Yes | Yes |  |  |  |  |  |  |  |
| Contractors | Measures | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | Status |
|  | companies inducted | 65 | 37 |  |  |  |  |  |  |  |
|  | companies audited |  | 12 |  |  |  |  |  |  |  |
|  | Staff Iunducted | 170 | 130 |  |  |  |  |  |  |  |
|  | Measures | Q1 Target | Q1 Actual | Q2 Target | Q2 Actual | Q3 Target | Q3 Actual | Q4 Target | Q4 Actual | Status |
|  | Audit Completed |  | X |  |  |  | x |  |  |  |
|  | Inductions Completed |  | 45 |  | 85 |  | 24 |  |  |  |
|  | Individuals not having Inductions Completed |  | 9 |  |  |  | 2 |  |  |  |
|  | Conpanies having Staff Inducted |  | 16 |  | 21 |  | 9 |  |  |  |
|  | Companies not having Inductions Completed |  | 3 |  |  |  | 1 |  |  |  |
| Status |  |  |  |  |  |  |  |  |  |  |
|  | Improved compliance |  |  |  |  |  |  |  |  |  |
|  | No change in compliance |  |  |  |  |  |  |  |  |  |
|  | Drop in compliance |  |  |  |  |  |  |  |  |  |